COOLING TOWER MOTOR CONTROL PANEL

- Furnish a NEMA 4 rated motor control panel completely wired with a fused control power transformer, cover mounted lockable main disconnect.  Motor control panel shall be free-standing, floor-mounted control enclosure. Configure cabinet for bottom entry of cables with all 120V control and communication wire segregated from 460V power wiring.  Internal wiring shall have type written conductor labels on all internal cabinet wiring. Labels shall correspond to the cabinet wiring diagrams and schematics. Text shall not be less than ¼” in height. Control Panel shall include a BACnet over MS/TP gateway communication card capable of interfacing with the Building Management System (BMS).

- Motor control panel shall have a touch screen view panel HMI.  The HMI should be capable of providing information on local programming and remote programming from the BMS for the following items:

- Cold Water Temperature (provided by RTD probe Section E)

- Cold Water Set Point

- Individual Motor Hand-Off-Auto selector

- PID Output Reference Indicator

- Tower Remote Enable/Disable selector

- VFD Bypass On/Off Indicator

- Remote Temperature Set Point

- On/Off deadband for Multiple Fan Staging

- PID Loop Configuration and Programming

- Alarm Log (maintaining min. 24 hour history)

- Operational Cooling Trend Log (maintaining min. 1 hour history for PID monitoring)

- Each internally mounted combination motor starter/adjustable overload protector shall have an integral lockable circuit breaker to enable individual motor isolation for maintenance. Auxiliary relays (dry contacts)shall be provided and wired back to the BMS to provide indication if a motor has tripped or failed.

- Each motor control panel shall segregate I/O points to the PLC and VFD to keep cooling tower operating should a motor trip or fail. Thermal performance should not decrease by more than 10% with a motor failure at peak design requirements.

- A 24VDC coil shall be connected to each motor starter contactor to be interfaced with the BMS.

- Terminal blocks shall be provided for main power feed, individual fan motor connections, and any externally mounted control input and outputs. All final wiring from cooling tower mounted junction box or disconnects to terminal strips located in motor control panel, and the main power feed to motor control panel, shall be completed in the field by others.

- Panel shall include a pre-programmed PLC (Programmable Logic Controller) capable of cold-water temperature monitoring, and cooling tower fan motor control. The PLC shall have a door mounted operator interface panel. Fan motor control consists of staging (energizing) fan motors (at full speed), beginning from the sump end of the tower, until the correct numbers of fans are operational to maintain the desired cold water set point temperature.  Partitioning shall be accomplished so that the loss of any one I/O card (input or output, or discrete or analog) will result in the loss of no more than three cooling towers’ cell control.

- A separate (4-20 ma, scale 30-200 Degrees f) temperature RTD probe, with 1/2" NPT male connection and 3/4" NPT male stainless steel thermal well, shall be supplied loose for field installation in the cooling tower cold water piping. The probe shall be wired back to the control panel, using 3-wire shielded cable, to provide a cold water temperature signal for proper fan staging control.

- Control Panel shall be equipped with a (4-20ma scale, 30-200 Degrees F) cold-water temperature "Remote Set Point" input. This feature allows the cold water temperature set point to be modified via the BMS. This overrides cold-water set point manually input (default) via the operator interface panel at the Control Panel. In the event the BMS signal is lost, the PLC control reverts back to default set point.

- The control panel shall be equipped for operating with a Variable Frequency Drive (VFD) Danfoss, ABB or equal. The PLC shall be equipped with a (0-10VDC or 4-20ma, scale 0- 100% Range) fan motor "Speed" output. This feature shall modify fan motor speeds to maintain desired cold-water temperature and maximize energy savings. All eight (8) fan motors shall be operated by a single VfD wired to the control panel input power disconnect, operating all fans in unison, providing airflow across entire tower fill media. When the VFO Bypass is engaged, or drive failure occurs, the PLC shall deenergize all fan motor starters, and begin a "Fan Staging" sequence of operation with fan motors operating at full speed. Note: When VFD input to panel is used, a separate 120V circuit must be provided for control power to the Control Panel.

COOLING TOWER VARIABLE FREQUENCY DRIVE

- All Variable Frequency Drives (VFD's) shall be sized according to Total Connected Full Load Amps (including all applicable factors required by governing Electrical Codes), not total connected horsepower.

- VFD shall be UL listed with a maximum ambient temperature of 40°C at an elevation less than 2,000 feet above sea level.

- Variable Frequency Drives (VFD's) shall be mounted indoors and shall be NEMA 3R Enclosure rated with electronic bypass.

  - Automatic bypass – three contactor type

  - Danfoss or ABB to be the manufacturer

  - A removable HMI programming keypad

  - RS-285 access port

  - 3% line reactors

  - DV/DT output filter

  - Circuit breaker type disconnect

  - Native Embedded Communication Protocol for BACnet over MSTP interface with the BMS.

  - Speed feedback: 4-20mA output signal from the drive to indicate motor speed.

  - Speed command: 4-20mA input signal from the cooling tower control panel to command the motor speed.

  - Internal PID Loop for backup to the cooling tower control panel.

- The complete bypass system hand-off-auto with inverter-bypass selector switches shall be packaged with the VFD. The unit shall be setup for automatic bypass operation upon VFD trip.

- VFD Cabinet shall have a On/Auto/Bypass Switch.  Drive can be operated by programming set on local interface on drive keypad.   Switch in “Off” position: Drive shall stop equipment without delay regardless of control inputs. Switch in “Auto” position: Drive shall be controlled by hardwired interface to control system.